## CTQ Guide (2)
Template | Equipment ID | Equipment Type | Procedure | Question Group | Help Text | Question | Answer | Negative answer | Image | Image | GiNi help text | Help Document
Review Stage (Tentative) | Work Center ID | Type | Section | Category | Requirement | Description | Input |  | Evidence- Yes | Evidence- No | Measurement Instrument | Tolerance
Pre-Assembly | WC1 | Tank | Dimensional | Parts and Holes | Control panel support location | Side Face: Verify the distance between the tank wall and the front face of the support | Input |  |  |  | Tape Measure | ISO 2768-1 Grade C
Pre-Assembly | WC1 | Tank | Dimensional | Parts and Holes | Location of radiator mounting lugs on rear face | Rear Face: Verify the horizontal position relative to the center of the tank according to the drawing | Input |  |  |  | Tape Measure | ISO 2768-1 Grade C
Pre-Assembly | WC1 | Tank | Dimensional | Parts and Holes | Location of grounding terminals on front face | Front Face: Verify the horizontal and vertical position of each terminal according to the drawing | Input |  |  |  | Tape Measure | ISO 2768-1 Grade C
Pre-Assembly | WC1 | Tank | Dimensional | Holes and Studs | Dimensions of bushing holes | Bushings: Holes on the left and right sides of the front face | Input |  |  |  | Tape Measure / Gauge | ISO 2768-1 Grade C
Assembly | WC2 | Tank | Dimensional | Reinforcements | Location of reinforcements | Verify that the reinforcements are at the height specified in the drawing | Input |  |  |  | Tape Measure | ISO 2768-1 Grade C
Assembly | WC2 | Tank | Dimensional | Frame | Frame flatness and cleanliness | Verify the flatness of the frame | Input |  |  |  | Bubble Level | 1 mm/m
Assembly | WC2 | Tank | Dimensional | Frame | Frame flatness and cleanliness | Is Frame clean? | Yes/No | No |  | X | Bubble Level | 1 mm/m
Assembly | WC2 | Tank | Dimensional | Welding | Use the supporting image as a reference guide | Is Leak-tight or structural welds without interference | Yes/No | No |  | X | Visual Inspection | None
Assembly | WC2 | Tank | Dimensional | Tank Interior | Tank internal clearance measurements | Verify internal dimensions according to the drawings and corner-to-corner diagonals of the tank | Input |  |  |  | Tape Measure | ISO 2768-1 Grade C
Painting | WC3 | Tank | Painting | Paint Finish | None permitted | Do you see Paint buildup, runs, or weld spatter | Yes/No | Yes | X |  | Visual Inspection | None
Painting | WC3 | Tank | Painting | Paint Scheme | Use the locations highlighted in the guide image as a reference | What is the Average coating thickness on Side face | Input |  |  |  | Coating Thickness Gauge | -0% / +20%
Painting | WC3 | Tank | Painting | Paint Scheme | Use the locations highlighted in the guide image as a reference | What is the Average coating thickness on Rear face | Input |  |  |  | Coating Thickness Gauge | -0% / +20%
Painting | WC3 | Tank | Painting | Paint Scheme | Use the locations highlighted in the guide image as a reference | What is the Average coating thickness on Front face | Input |  |  |  | Coating Thickness Gauge | -0% / +20%
Markings | WC4 | Tank | Painting | Marking Finish | No stains around markings | Are there any marking stained around its border | Yes/No | Yes | X |  | Visual Inspection | None
Markings | WC4 | Tank | Painting | Marking Location | Center-of-gravity and shipping markings | Verify the correct location of the center-of-gravity markings | Input |  |  |  | Tape Measure | ISO 2768-1 Grade C
Markings | WC4 | Tank | Painting | Complete Markings | HV markings | Do you see HV markings markings ? | Yes/No | No |  | X | Visual Inspection | None
Assembly | WC5 | Cover | Dimensional | Bushings: Holes and Studs | Alignment of bushing studs | Verify that the studs are aligned horizontally | Yes/No | No |  | X | Gauge / Bubble Level | 1 mm/m
Assembly | WC5 | Cover | Dimensional | Bushings: Holes and Studs | Alignment of bushing studs | Verify that the studs are aligned vertically | Yes/No | No |  | X | Gauge / Bubble Level | 1 mm/m
Assembly | WC5 | Cover | Dimensional | Surface Finish | There must be no sharp edges, burrs, or rough corners | Are there any Rounded sharp edges; burr-free edges and corners | Yes/No | Yes | X |  | Visual Inspection | None
Painting | WC6 | Cover | Painting | Surface Finish | None permitted | Do you see Paint buildup, runs, or weld spatter | Yes/No | Yes | X |  | Visual Inspection | None
Painting | WC6 | Cover | Painting | Paint Scheme | Average coating thickness on the left side of the front face | Take 12 measurements distributed across the face | Input |  |  |  | Coating Thickness Gauge | -0% / +20%
Painting | WC7 | Accessories | Painting | Surface Finish | None permitted | Do you see Paint buildup, runs, or weld spatter | Yes/No | Yes | X |  | Visual Inspection | None
Painting | WC7 | Accessories | Painting | Paint Scheme | Paint thickness | Take 2 measurements on each accessory | Input |  |  |  | Coating Thickness Gauge | -0% / +20%
Markings | WC8 | Accessories | Painting | Complete Markings | Grounding marking | Do you see All unpainted areas include a grounding marking, with no surrounding stains, sharp borders, and an appropriate size | Yes/No | No |  | X | Visual Inspection | None

## Sheet1
|  | ET | E ID | Template | R. G
|  | Tank | WC1 | Pre-Assembly | WC1
|  | Tank | WC2 | Assembly | WC2
|  | Tank | WC3 | Painting | WC3
|  | Tank | WC4 | Markings | WC4
EID | Template | R. G | Resrc | Resrc
Wc2 | Pre-Assembly | WC1 | Bob | Jack
| Assembly | WC2 | Ritesh
| Painting | WC3 | Tom
| Markings | WC4 | Barry | Frank
| EID | ET | Template | # of Questions | RSRC | R G
| WC1 | Tank | Pre-Assembly | 5 | Bob | Pre-Assembly
| WC2 | Tank | Assembly | 3 |  | Assembly
| WC3 | Tank | Painting | 2 |  | Painting
| WC4 | Tank | Markings | 6 | Jack | Markings
| EID | ET | Template | # of Questions | RSRC | R G
| FL1 | Forklift | Temp1 | 3 | Bob | Mech
| FL1 | Forklift | Temp2 | 10 | Jack | Sup
| FL1 | Forklift | Temp3 | 20 | Tom | Operator
| FL2 | Forklift | Temp1 | 3 | Bob | Mech